## Slide 1
Optimization and prediction of the energy consumption of a school building in Turin
ICT in Building Design
Team 4
Professors:
Giacomo Chiesa
Lorenzo Bottaccioli
Arman Mohammadigilani
Mohammad Eftekhari Pour
Hossein Zahedi Nezhad
Setareh Pourgholamali
Ali Mohammad Alizadeh
Authors:

## Slide 2
Table of contents
02.
Surrogate Model
01.
Overview
04.
Energy Signature
03.
Data Dashboard
2
05.
Prediction

## Slide 3
Overview
1
3

## Slide 4
Improve the energy efficiency of the school building in Turin:
4
Optimize the IDF (Input Data File) using a Surrogate Design Optimization model through DesignBuilder for enhanced energy efficiency in Turin's school building.
Implement intelligent control strategies for virtual monitoring of the building's behavior, utilizing real-time data and feedback.
Optimize energy management to improve overall efficiency.
Objectives

## Slide 5
5
IDF
EPW
Surrogate Design Optimization
Parameter Optimization
Surrogate Model Deployment
Design of Experiment
Optimized
IDF
System Framework

## Slide 6
6
Optimized
IDF
EPW
Building Management System
Sensors
Actuator
Device Connector
Data Storage and Dashboard
Prediction Algorithm
Energy Signature
Stepped Simulation with I/O
System Framework

## Slide 7
7
Type | School
Location | Turin
Details | 4 Classrooms, 2 Offices, 3 Toilets, 1 Corridor, 1 Storage Room, 1 Reception Room
Specified Parameters
CoolingFuel: Electricity from grid
Cooling Set Point: 26-30
Heating Fuel: Natural Gas
Heating Set Point: 16-20
Humidification set points: 30-50 %
Window Type: Double Glazing
Illuminance: 500 lux
Lighting: LED
Radiant_Visible fraction: 0.420-0.180
schedule: 7:00-18:00 (Monday-Friday)
Ventilation: ON
DesignBuilder

## Slide 8
8
Surrogate Model
2

## Slide 9
9
Surrogate Model Sampling
Create 100 samples using different combinations of the following 4 parameters using the IDF and EPW files:
Insulation Thickness (0.01 - 0.35 m)
ACH (0 – 6 ACH)
Irradiation Setpoint (80 – 300 W/)
Temperature Setpoint (18 – 28 )
District Heating
District Cooling
Electricity Facility
Objectives:

## Slide 10
10
3D Analysis of Electricity vs. Heating and Cooling Demands
Data Distribution:
  Blue Crosses: Spread along cooling and heating axes; tighter clustering on electricity axis.
  Implication: Building design/operation impacts heating/cooling more than electricity.
Pareto Optimal Points (Red Dots):
  Located primarily at lower values for all energy demands.
  Significance: Efficient configurations minimize all energy types simultaneously.
Trends and Trade-offs:
  Non-linear correlation between cooling/heating and electricity demands.
  Potential: Reducing heating/cooling could proportionally decrease electricity usage.

## Slide 11
11
Relationships between building parameters and energy consumptions
Insulation Thickness:
  Heating Demand: Strongly negative correlation; enhances thermal resistance.
  Cooling/Electricity Demand: Minimal to slight increase due to trapped heat.
Irradiation:
  Electricity Demand: Strongly negative; less need for artificial lighting.
  Cooling Demand: Increases with more sunlight, complicating energy management.
ACH (Air Changes per Hour):
  Cooling Demand: Negative correlation; more air changes reduce mechanical cooling needs.
  Trade-off: Excessive ACH can increase energy consumption by removing conditioned air.
Seasonal Demand Variations:
  Inverse Relationship: Heating increases in colder months, cooling in warmer months; crucial for adaptive energy management strategies.

## Slide 12
12
Insulation Thickness | Irradiation | Temperature | ACH
0.347823 | 81.923858 | 19.256269 | 5.597644
Electricity [J] | DistrictHeating [J] | DistrictCooling [J] | Total [J]
1.404403e+10 | 1.430754e+10 | 1.163074e+10 | 3.998231e+10
Optimize Parameters:
Design Optimization
Objective Parameters:
Electricity:Facility | DistrictHeating:Facility | DistrictCooling:Facility
0.000059 | 1.264588 | 0.460608
MAE values for the problem objectives:

## Slide 13
13
Data Dashboard
3

## Slide 14
Real-time interaction and data exchange
Optimized IDF and EPW files for parameter.
Stepped Simulation with I/O in EnergyPlus GYM
14
Simulation and Data Visualization
Data collection via sensors
Using MQTT protocol for data transmission.
Building Management System Framework

## Slide 15
15
Grafana Dashboard

## Slide 16
16
Energy Signature
4

## Slide 17
Its diagram is a widely used instrument for analysis and prediction of energy use in the buildings.
Energy signature represents the energy behavior of a building by correlating energy consumption with climatic variables.
17
Energy Signature
Figure parameters
Power [Kw] vs T
Analysis method
OLS
(Ordinary Least Square)

## Slide 18
Energy Signature for Summer and Winter
18

## Slide 19
19
Energy Signature / R-squared for Regression
 | Winter Hourly | Winter Daily | Winter Weekly | Winter Monthly
 | 0.344 | 0.482 | 0.676 | 0.821
 | -0.243 | -0.323 | -0.231 | -0.248
 | Winter Hourly | Winter Daily | Winter Weekly | Winter Monthly
 | 0.344 | 0.482 | 0.676 | 0.821
 | -0.243 | -0.323 | -0.231 | -0.248
 | Summer Hourly | Summer Daily | Summer Weekly | Summer Monthly
 | 0.372 | 0.438 | 0.537 | 0.609
 | 0.192 | 0.140 | 0.186 | 0.315
 | Summer Hourly | Summer Daily | Summer Weekly | Summer Monthly
 | 0.372 | 0.438 | 0.537 | 0.609
 | 0.192 | 0.140 | 0.186 | 0.315

## Slide 20
20
Prediction
5

## Slide 21
Type: Advanced Recurrent Neural Network (RNN) architecture.
Purpose: Specifically designed for effective modeling of sequential data.
LSTM (Long Short-Term Memory)
21
Handles time series and other sequential data.
Incorporates memory cells to maintain and update information over time.
Overcomes vanishing gradient problems, improving learning stability and performance.
Captures long-term dependencies to enhance training accuracy.
Prediction

## Slide 22
22
Validation and Training losses for Heating and Cooling consumptions
Lags | Step ahead | Epochs | Batch size | RMSE | MAE
72 | 3 | 50 | 32 | 1.52e+06 | 1.52e+06
72 | 3 | 50 | 32 | 1.94e+06 | 0.66e+06
72 | 3 | 60 | 64 | 1.34e+06 | 0.54e+06
72 | 3 | 60 | 64 | 1.86e+06 | 0.78e+06
Lags | Step ahead | Epochs | Batch size | RMSE | MAE
72 | 3 | 60 | 32 | 2.76e+06 | 1.58e+06
72 | 3 | 60 | 32 | 3.94e+06 | 1.76e+06
72 | 3 | 60 | 64 | 1.24e+06 | 0.88e+06
72 | 3 | 60 | 64 | 2.82e+06 | 1.35e+06
Heating
Cooling

## Slide 23
23
Cooling and Heating consumption prediction with monthly view

## Slide 24
Do you have any questions?